## Calculator
Objective
This model evaluates a 'flexible' minimum qualifying criteria for the DX Units measure in the MN HVAC&R program.
Overview | [10 empty] | Solve for SEER_proposed given EER_proposed (photo)
The flexible minimum qualifying concept increases the range of qualified DX Unit equipment by accepting equipment with lower EERs (full-load efficiency) and higher SEERs (part-load efficiency). This alternative qualifying method was inspired by trade partner feedback regarding rejections of prescriptive DX Unit applications for equipment that barely failed to meet minimum qualifying full-load efficiencies while substantially exceeding minimum qualifying part-load efficiencies. The concept uses a single result, Total Electric ARR$, to determine if candidate equipment results in more Total Electric ARR$ than would occur under the current minimum qualifying rules. Instead of setting the minimum qualifying values using static minimum qualifying part-load and full-load efficiencies, the minimum qualifying criteria is defined as: The equipment efficiencies are greater or equal to baseline values AND the Total Utility Electric ARR $ with the Flexible Rules is greater than the Total Utility Electric ARR $ from the same measure using minimum qualifying values as inputs (the "Minimum Qualifying" scenario). Effectively, the flexible minimum qualifying concept is using a single result, Total Electric ARR$, instead of two results, kW & kWh, to quantify and then compare the value of the savings to the utility for a given piece of equipment.
Inputs |  |  |  |  | Calculation Parameters
Parameter | Value | Baseline / Code Minimum | Min Qualifying |  | Parameter | Value
Building Type | Lodging |  |  |  | Min_EER__c | 10.9
Cooling Capacity (Tons) | 32.5 |  |  |  | Min_SEER__c | 12
Full Load Efficiency (EER) | 10.7 | 9.8 | 10.9 |  | EER_Baseline__c | 9.8
Part Load Efficiency (SEER) | 15.9 | 9.9 | 12 |  | SEER_Baseline__c | 9.9
County | Isanti MN2 |  |  |  | P_Cooling_Hrs_mc4__c | 606
NewModel | MN - RTUS - 20 - 63.33 tons |  |  |  | Rebate_Bonus_Full_Load__c | 4
[5 empty] | Rebate_Bonus_Part_Load__c | 3
Results |  |  |  |  | Rebate_Step_Qualifier__c | 0.1
| Results - Minimum Qualifying | Results - Current Rules | Results - Flexible Rules |  | Coincidence_Factor__c | 0.9
EER Pass? | N/A | FAIL | PASS |  | Conversion_Factor__c | 0 |  | Example Equipment
IEER Pass? | N/A | PASS | PASS |  | Incremental_Cost_per_Ton__c | 189
Pass / Fail | N/A | FAIL | PASS |  | eo3__Maximum_Rebate_Currency__c | 50
Customer Savings (kW) | 4.016 | 3.347 | 3.347 |  | ARR$_kW | 1491.0459
Customer Savings (kWh) | 4178 | 9009 | 9009 |  | ARR$_kWh | 0.45212
Customer Savings (PC kW) | 3.614 | 3.013 | 3.013 |  | Net_Gen_to_Customer | 1.0191
Net Gen kW | 3.9407 | 3.2842 | 3.2842 |  | one_table_index_row | 4
Net Gen kWh | 4257.8515 | 9181.1833 | 9181.1833 |  | county_lookup | MN2
Rebate - Size ($) | 1625 | 1625 | 1625
Rebate - Full Load ($) | 0 | -260 | -260
Rebate - Part Load ($) | 0 | 3802.5 | 3802.5
Rebate Total ($) | 1625 | 0 | 5167.5
Utility Electric kW ARR $ | 5875.7412 | 4896.9387 | 4896.9387
Utility Electric kWh ARR $ | 1925.0388 | 4150.9514 | 4150.9514
Total Utility Electric ARR $ | 7800.78 | 9047.89 | 9047.89
Minimum Qualifying ARR Values using 2021 'static' Rules
| < 5.4 tons | 5.4 - 11.3 tons | 11.4 - 19.9 tons | 20 - 63 tons | > 63 tons
eo3__Equipment_Type__c | MN - RTUS < 5.42 tons | MN - RTUS - 5.42 - 11.24 tons | MN - RTUS - 11.25 - 19.99 tons | MN - RTUS - 20 - 63.33 tons | MN - RTUS - 63.34 tons and above
Min_EER__c | 11.05 | 11.3 | 11.1 | 10.9 | 10.9
Min_SEER__c | 13.7 | 12.2 | 12.1 | 12 | 12
EER_Baseline__c | 11.05 | 11 | 10.8 | 9.8 | 9.5
SEER_Baseline__c | 13 | 11.2 | 11 | 9.9 | 9.6
Size_Max__c | 5.42 | 11.25 | 20 | 63.34 | 300
P_Cooling_Hrs_mc4__c | 598.5 | 598.5 | 598.5 | 598.5 | 598.5
Customer Savings (kW) | 0 | 0.326 | 0.601 | 7.827 | 48.672
Customer Savings (kWh) | 153 | 591 | 1187 | 8041 | 44888
Customer Savings (PC kW) | 0 | 0.293 | 0.541 | 7.044 | 43.805
Net Gen kW | 0 | 0.33223 | 0.61249 | 7.9766 | 49.6022
Net Gen kWh | 155.9242 | 602.2954 | 1209.6864 | 8194.6825 | 45745.9159
Utility Electric kW ARR $ | 0 | 495.3711 | 913.2456 | 11893.4658 | 73959.214
Utility Electric kWh ARR $ | 70.4957 | 272.3068 | 546.9174 | 3704.9395 | 20682.4182
Total Utility Electric ARR $ | 70.4957 | 767.678 | 1460.163 | 15598.4053 | 94641.6322
Minimum Qualified ARR $/Ton | 13.0066 | 68.238 | 73.0082 | 246.2647 | 315.4721
SEER vs. EER Table for Flexible Minimum Qualifying Rules - Direct Calculation
EER | < 5.4 tons | 5.4 - 11.3 tons | 11.4 - 19.9 tons | 20 - 63 tons | > 63 tons
9 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.1 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.2 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.3 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.4 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.5 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 113.2068
9.6 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 67.225
9.7 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 48.0934
9.8 | Not Qualified | Not Qualified | Not Qualified | 37.607 | 37.6087
9.9 | Not Qualified | Not Qualified | Not Qualified | 30.9882 | 30.9893
10 | Not Qualified | Not Qualified | Not Qualified | 26.4296 | 26.4305
10.1 | Not Qualified | Not Qualified | Not Qualified | 23.0989 | 23.0995
10.2 | Not Qualified | Not Qualified | Not Qualified | 20.5588 | 20.5593
10.3 | Not Qualified | Not Qualified | Not Qualified | 18.5577 | 18.5582
10.4 | Not Qualified | Not Qualified | Not Qualified | 16.9406 | 16.9409
10.5 | Not Qualified | Not Qualified | Not Qualified | 15.6065 | 15.6068
10.6 | Not Qualified | Not Qualified | Not Qualified | 14.4871 | 14.4874
10.7 | Not Qualified | Not Qualified | Not Qualified | 13.5345 | 13.5347
10.8 | Not Qualified | Not Qualified | 14.525 | 12.714 | 12.7142
10.9 | Not Qualified | Not Qualified | 13.6004 | 11.9998 | 12
11 | Not Qualified | 14.5635 | 12.8003 | 11.3726 | 11.3728
11.1 | 13.291 | 13.6654 | 12.1012 | 10.8174 | 10.8176
11.2 | 13 | 12.8849 | 11.4852 | 10.3225 | 10.3226
11.3 | 13 | 12.2005 | 11 | 9.9 | 9.8787
11.4 | 13 | 11.5953 | 11 | 9.9 | 9.6
11.5 | 13 | 11.2 | 11 | 9.9 | 9.6
11.6 | 13 | 11.2 | 11 | 9.9 | 9.6
11.7 | 13 | 11.2 | 11 | 9.9 | 9.6
11.8 | 13 | 11.2 | 11 | 9.9 | 9.6
11.9 | 13 | 11.2 | 11 | 9.9 | 9.6
12 | 13 | 11.2 | 11 | 9.9 | 9.6
12.1 | 13 | 11.2 | 11 | 9.9 | 9.6
12.2 | 13 | 11.2 | 11 | 9.9 | 9.6
12.3 | 13 | 11.2 | 11 | 9.9 | 9.6
12.4 | 13 | 11.2 | 11 | 9.9 | 9.6
12.5 | 13 | 11.2 | 11 | 9.9 | 9.6
12.6 | 13 | 11.2 | 11 | 9.9 | 9.6
12.7 | 13 | 11.2 | 11 | 9.9 | 9.6
12.8 | 13 | 11.2 | 11 | 9.9 | 9.6
12.9 | 13 | 11.2 | 11 | 9.9 | 9.6
13 | 13 | 11.2 | 11 | 9.9 | 9.6
Derive Coefficients for Salesforce Calculator Build
eo3__Equipment_Type__c | MN - RTUS < 5.42 tons | MN - RTUS - 5.42 - 11.24 tons | MN - RTUS - 11.25 - 19.99 tons | MN - RTUS - 20 - 63.33 tons | MN - RTUS - 63.34 tons and above
Formula - ARR/Ton as a function of EER: | =1/(-((B$50/(12*Calculator!Net_Gen_to_Customer))-(1/B$38-1/$A55)*Calculator!ARR__kW)/(Calculator!ARR__kWh*B$41)+1/B$39) | =1/(-((C$50/(12*Calculator!Net_Gen_to_Customer))-(1/C$38-1/$A55)*Calculator!ARR__kW)/(Calculator!ARR__kWh*C$41)+1/C$39) | =1/(-((D$50/(12*Calculator!Net_Gen_to_Customer))-(1/D$38-1/$A55)*Calculator!ARR__kW)/(Calculator!ARR__kWh*D$41)+1/D$39) | =1/(-((E$50/(12*Calculator!Net_Gen_to_Customer))-(1/E$38-1/$A55)*Calculator!ARR__kW)/(Calculator!ARR__kWh*E$41)+1/E$39) | =1/(-((F$50/(12*Calculator!Net_Gen_to_Customer))-(1/F$38-1/$A55)*Calculator!ARR__kW)/(Calculator!ARR__kWh*F$41)+1/F$39)
ARR/Ton as a function of EER: | -24.6342 | -23.4438 | -30.1235 | -42.7541 | -42.7519
-24.6342
iCoef0 | 1.0636 | 5.5799 | 5.9699 | 20.1372 | 25.7963
iCoef1 | 134.9363 | 135.5496 | 138.0598 | 152.1475 | 156.9522
iCoef2 | 270.5909 | 270.5909 | 270.5909 | 270.5909 | 270.5909
iCoef3 | 0.076923 | 0.089286 | 0.090909 | 0.10101 | 0.10417
iCoef4 | 1491.0459 | 1491.0459 | 1491.0459 | 1491.0459 | 1491.0459
Simplified Formula - ARR/Ton as a function of EER | -24.6342 | -23.4438 | -30.1235 | -42.7541 | -42.7519
| =1/(-(B103-(B104-B107/$A55))/B105+B106) | =1/(-(C103-(C104-C107/$A55))/C105+C106) | =1/(-(D103-(D104-D107/$A55))/D105+D106) | =1/(-(E103-(E104-E107/$A55))/E105+E106) | =1/(-(F103-(F104-F107/$A55))/F105+F106)
1/(-(B102-(B103-B106/EER_input))/B104+B105)
SEER vs. EER Curve Coefficients Validation - 1/(-(B102-(B103-B106/EER_input))/B104+B105)
| Direct Calculation | Curve Fit | Direct Calculation | Curve Fit | Direct Calculation | Curve Fit | Direct Calculation | Curve Fit | Direct Calculation | Curve Fit
EER | MN - RTUS < 5.42 tons | MN - RTUS < 5.42 tons | MN - RTUS - 5.42 - 11.24 tons | MN - RTUS - 5.42 - 11.24 tons | MN - RTUS - 11.25 - 19.99 tons | MN - RTUS - 11.25 - 19.99 tons | MN - RTUS - 20 - 63.33 tons | MN - RTUS - 20 - 63.33 tons | MN - RTUS - 63.34 tons and above | MN - RTUS - 63.34 tons and above
Minimum ARR$/Ton |  | 13.0066 |  | 68.238 |  | 73.0082 |  | 246.2647 |  | 315.4721
9 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.1 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.2 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.3 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.4 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified
9.5 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 113.2068 | 113.2068
9.6 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 67.225 | 67.225
9.7 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 48.0934 | 48.0934
9.8 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 37.607 | 37.607 | 37.6087 | 37.6087
9.9 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 30.9882 | 30.9882 | 30.9893 | 30.9893
10 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 26.4296 | 26.4296 | 26.4305 | 26.4305
10.1 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 23.0989 | 23.0989 | 23.0995 | 23.0995
10.2 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 20.5588 | 20.5588 | 20.5593 | 20.5593
10.3 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 18.5577 | 18.5577 | 18.5582 | 18.5582
10.4 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 16.9406 | 16.9406 | 16.9409 | 16.9409
10.5 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 15.6065 | 15.6065 | 15.6068 | 15.6068
10.6 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 14.4871 | 14.4871 | 14.4874 | 14.4874
10.7 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 13.5345 | 13.5345 | 13.5347 | 13.5347
10.8 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 14.525 | 14.525 | 12.714 | 12.714 | 12.7142 | 12.7142
10.9 | Not Qualified | Not Qualified | Not Qualified | Not Qualified | 13.6004 | 13.6004 | 11.9998 | 11.9998 | 12 | 12
11 | Not Qualified | Not Qualified | 14.5635 | 14.5635 | 12.8003 | 12.8003 | 11.3726 | 11.3726 | 11.3728 | 11.3728
11.1 | 13.291 | 13.291 | 13.6654 | 13.6654 | 12.1012 | 12.1012 | 10.8174 | 10.8174 | 10.8176 | 10.8176
11.2 | 13 | 13 | 12.8849 | 12.8849 | 11.4852 | 11.4852 | 10.3225 | 10.3225 | 10.3226 | 10.3226
11.3 | 13 | 13 | 12.2005 | 12.2005 | 11 | 11 | 9.9 | 9.9 | 9.8787 | 9.8787
11.4 | 13 | 13 | 11.5953 | 11.5953 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
11.5 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
11.6 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
11.7 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
11.8 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
11.9 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.1 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.2 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.3 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.4 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.5 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.6 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.7 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.8 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
12.9 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
13 | 13 | 13 | 11.2 | 11.2 | 11 | 11 | 9.9 | 9.9 | 9.6 | 9.6
| 260.291 | 260.291 | 244.1097 | 244.1097 | 262.5121 | 262.5121 | 453.2352 | 453.2352 | 676.6463 | 676.6463
Ref:
Note on A11: Matt Chmielewski: Affects the EFLH value to be used.
Note on D15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EER and SEER efficiencies must be greater or equal to Baseline/Code Minimum values, but do NOT have to be greater or equal to Min Qualifying values.
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 'PASS' means the equipment efficiencies are greater or equal to baseline values AND the Total Utility Electric ARR $ with the Flexible Rules is greater than the Total Utility Electric ARR $ of the "Minimum Qualifying" scenario.
Note on D25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Efficiencies that are below min qualifying but above baseline will generate a negative rebate$ amount. It seems appropriate to penalize the total rebate if the equipment does not meet minimum qualifying values.
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Alternative Formula: =ROUND((Program_Measure__r.eo3__Maximum_Rebate_Currency__c+((I_EER_MC04__c-Project_Measure__r.eo3__Equipment_Model__r.Min_EER__c)/Program_Measure__r.Rebate_Step_Qualifier__c)*Program_Measure__r.Rebate_Bonus_Full_Load__c+((i_SEER_MC04__c-Project_Measure__r.eo3__Equipment_Model__r.Min_SEER__c)/Program_Measure__r.Rebate_Step_Qualifier__c)*Program_Measure__r.Rebate_Bonus_Part_Load__c)*i_unit_cooling_tons_mc__c*1,2)
Note on A41: Matt Chmielewski: A single value is used to define EFLH (P_Cooling_Hrs) for all equipment. The value is based on the quantity-weighted average for this input across measure history. It can be referenced as "=Historical_mean_of_medians_EFLH" Note that a SEER-EER table was originally generated and filed with the state using 598.5 EFLH. Ideally, the calculated weighted average from history would be used, but in this case the value already filed will be used here 6/24/2021.